======================================================================

DIGITALLY DEFINED

ASSEMBLY STANDARDS LIBRARY

ASSEMBLY ID:

ASM-201

ASSEMBLY NAME:

Single Cat6 Home Run Assembly

VERSION:

1.0

STATUS:

FROZEN

======================================================================

ASSEMBLY METADATA

Assembly Category

Data Infrastructure

--------------------------------------------------

Assembly Type

Structured Cabling

--------------------------------------------------

Difficulty Level

2 of 5

--------------------------------------------------

Required Crew

1 Low-Voltage Technician

--------------------------------------------------

Estimated Labor

Automatically Generated

Referenced from LAB Library

--------------------------------------------------

Required Skill Level

Level-1 Technician

--------------------------------------------------

Dependencies

PROD Library

MAT Library

LAB Library

ROOM Library

QC Library

ANSI/TIA Structured Cabling Standards

======================================================================

PURPOSE

The Single Cat6 Home Run Assembly establishes the standard

installation method for a single Category 6 data cable installed as

a dedicated home run from the device location to the Structured

Wiring Closet.

This assembly provides reliable high-speed connectivity while

maintaining consistency across every Digitally Defined installation.

======================================================================

STANDARD APPLICATIONS

Approved For

• Television Locations

• Wireless Access Points

• Security Devices

• Touchscreens

• Smart Thermostats

• Smart Appliances

• Camera Systems

• Network Equipment

• Future Expansion Locations

======================================================================

STANDARD SCOPE

This assembly includes:

• One Cat6 home run

• One low-voltage bracket

• Service loop at device

• Service loop at panel

• Cable identification

• Cable certification

• Photo documentation

======================================================================

STANDARD INSTALLATION

Install one continuous Cat6 cable from the device location to the

Structured Wiring Closet.

No splices shall be permitted.

Support cable using approved fastening methods without crushing or

deforming the cable jacket.

Maintain minimum separation from electrical wiring.

Protect cable from physical damage throughout installation.

======================================================================

CABLE REQUIREMENTS

Cable Type

Category 6

--------------------------------------------------

Topology

Home Run

--------------------------------------------------

Maximum Length

90 Meters (295 Feet)

Permanent Link

--------------------------------------------------

Termination

TIA-568B

Unless project documents specify otherwise.

======================================================================

INSTALLATION REQUIREMENTS

Maintain minimum bend radius:

4x Cable Diameter

--------------------------------------------------

Avoid excessive pulling force.

--------------------------------------------------

Do not staple through cable.

--------------------------------------------------

Maintain service loops:

Device End

12"

Panel End

36"

======================================================================

REQUIRED PRODUCTS

Automatically Generated

Referenced from:

PROD Library

======================================================================

REQUIRED MATERIALS

Automatically Generated

Referenced from:

MAT Library

Typical materials include:

• Cat6 Cable

• Cable Labels

• J-Hooks

• D-Rings

• Velcro Straps

• Low-Voltage Bracket

• Faceplate

• Keystone Jack

======================================================================

REQUIRED LABOR

Automatically Generated

Referenced from:

LAB Library

Typical operations include:

• Layout

• Pull Cable

• Secure Cable

• Install Bracket

• Label Cable

• Terminate Cable

• Certification Test

• Photograph Installation

• QC Inspection

======================================================================

REQUIRED TOOLS

• Fish Tape

• Cable Puller

• Label Printer

• Punch Down Tool

• Cable Jacket Stripper

• Cable Certification Tester

• Tone Generator

======================================================================

SAFETY & PPE REQUIREMENTS

Required PPE

□ Safety Glasses

□ Gloves

□ Dust Mask

Safety Requirements

• Protect cable from sharp edges.

• Follow ladder safety procedures.

• Restore fire-rated penetrations.

• Maintain separation from electrical systems.

======================================================================

QUALITY CONTROL

Verify:

□ Continuous home run

□ No splices

□ Proper support

□ Proper bend radius

□ Proper labeling

□ Correct service loops

□ Certified cable test passed

□ Photo documentation complete

======================================================================

INSPECTION & ACCEPTANCE CRITERIA

PASS when:

□ Cable certification passes

□ Labels match documentation

□ Service loops provided

□ Cable undamaged

□ Photos uploaded

FAIL when:

□ Failed certification

□ Cable splice found

□ Crushed cable

□ Missing labels

□ Missing documentation

======================================================================

LIFECYCLE MANAGEMENT

Expected Service Life

25+ Years

--------------------------------------------------

Preventive Maintenance

None Required

--------------------------------------------------

Replacement Criteria

Replace upon failed certification or physical damage.

--------------------------------------------------

Field Repairability

Replace Entire Home Run

(No splicing permitted.)

--------------------------------------------------

Warranty Classification

Permanent Infrastructure

======================================================================

TRAINING REQUIREMENTS

Minimum Technician Level

Level-1 Technician

--------------------------------------------------

Required Certifications

Structured Cabling Certification

--------------------------------------------------

Required Hands-On Demonstration

Yes

--------------------------------------------------

Field Sign-Off Required

Yes

--------------------------------------------------

Estimated Training Time

3 Hours

--------------------------------------------------

Related Training Modules

Cable Pulling

Cable Routing

Termination

Cable Certification

--------------------------------------------------

Competency Test Required

YES

======================================================================

ROOM COMPATIBILITY

Compatible with all ROOM Standards requiring a

single network drop.

======================================================================

UPGRADE COMPATIBILITY

Compatible With:

• ASM-202 Dual Cat6

• ASM-203 Quad Cat6

• ASM-204 Six Cat6

• ASM-205 Fiber Backbone

• ASM-207 Wireless Access Point

• ASM-501 Camera Systems

======================================================================

INSTALLATION RULES

1.

Every Cat6 cable shall be a continuous home run.

--------------------------------------------------

2.

No splices shall be permitted.

--------------------------------------------------

3.

Every cable shall be certified after termination.

--------------------------------------------------

4.

Every cable shall receive permanent identification

labels at both ends.

--------------------------------------------------

5.

Only approved Cat6 cable shall be installed.

--------------------------------------------------

6.

Every completed assembly shall include photo

documentation.

======================================================================

COMMON ERRORS TO AVOID

• Cable kinks

• Over-tightened zip ties

• Improper bend radius

• Missing labels

• Failed certification

• No service loops

• Routing near electrical wiring

• Stapled cable

• Missing QC photographs

======================================================================

REFERENCED LIBRARIES

DD-058 Assembly Standards Library

PROD Library

MAT Library

LAB Library

ROOM Library

QC Library

ANSI/TIA-568 Standards

Installation Standards

======================================================================

REVISION APPROVAL

Engineering Approval

________________________

Operations Approval

________________________

Effective Date

________________________

Supersedes Version

N/A

Change Summary

Initial Release

======================================================================

END OF ASSEMBLY

ASM-201

======================================================================