======================================================================

DIGITALLY DEFINED

ASSEMBLY STANDARDS LIBRARY

ASSEMBLY ID:

ASM-203

ASSEMBLY NAME:

Quad Cat6 Home Run Assembly

VERSION:

1.0

STATUS:

FROZEN

======================================================================

ASSEMBLY METADATA

Assembly Category

Data Infrastructure

--------------------------------------------------

Assembly Type

High-Density Structured Cabling

--------------------------------------------------

Difficulty Level

3 of 5

--------------------------------------------------

Required Crew

1 Low-Voltage Technician

--------------------------------------------------

Estimated Labor

Automatically Generated

Referenced from LAB Library

--------------------------------------------------

Required Skill Level

Level-2 Technician

--------------------------------------------------

Dependencies

PROD Library

MAT Library

LAB Library

ROOM Library

QC Library

ANSI/TIA-568 Standards

======================================================================

PURPOSE

The Quad Cat6 Home Run Assembly establishes the standard

installation for four dedicated Category 6 home run cables

terminated at a single device location.

This assembly is the preferred standard for premium television

locations, media rooms, home offices, structured AV systems, and

future-ready installations requiring maximum flexibility.

======================================================================

STANDARD APPLICATIONS

Approved For

• Premium Television Locations

• Media Rooms

• Home Offices

• Equipment Cabinets

• Smart Home Controllers

• Network Distribution Points

• Luxury Living Rooms

• Commercial AV Locations

======================================================================

STANDARD SCOPE

This assembly includes:

• Four Cat6 home runs

• One low-voltage bracket

• Device-end service loops

• Panel-end service loops

• Permanent cable identification

• Cable certification

• Photo documentation

======================================================================

STANDARD INSTALLATION

Install four continuous Cat6 cables from the device location to the

Structured Wiring Closet.

Route all four cables together whenever practical while maintaining

proper bend radius and avoiding excessive bundle compression.

No splices shall be permitted.

Protect cables from physical damage throughout the installation.

======================================================================

CABLE REQUIREMENTS

Cable Type

Category 6

--------------------------------------------------

Topology

Quad Home Run

--------------------------------------------------

Maximum Length

90 Meters (295 Feet)

Per Cable

--------------------------------------------------

Termination

TIA-568B

Unless otherwise specified.

======================================================================

INSTALLATION REQUIREMENTS

Maintain minimum bend radius:

4x Cable Diameter

--------------------------------------------------

Maximum bundle tension shall not exceed manufacturer

recommendations.

--------------------------------------------------

Support cable using approved J-hooks, D-rings, or

structured cable supports.

--------------------------------------------------

Service Loops

Device End

12"

Panel End

36"

======================================================================

REQUIRED PRODUCTS

Automatically Generated

Referenced from:

PROD Library

======================================================================

BILL OF MATERIALS (BOM)

Referenced Automatically

PROD Library

MAT Library

LAB Library

Typical References

PROD-XXXX   Category 6 Cable

PROD-XXXX   Keystone Jack

PROD-XXXX   Faceplate

MAT-XXXX    Cable Labels

MAT-XXXX    Velcro Straps

MAT-XXXX    Cable Supports

LAB-XXXX    Pull Quad Cat6

LAB-XXXX    Terminate Cat6

LAB-XXXX    Certification Testing

======================================================================

REQUIRED MATERIALS

Automatically Generated

Referenced from:

MAT Library

Typical materials include:

• Category 6 Cable

• Cable Labels

• Velcro Straps

• Low-Voltage Bracket

• Keystone Jacks

• Faceplate

======================================================================

REQUIRED LABOR

Automatically Generated

Referenced from:

LAB Library

Typical operations include:

• Layout

• Pull Quad Cat6

• Secure Bundle

• Install Bracket

• Terminate Four Cables

• Label All Cables

• Certification Testing

• Photograph Installation

• QC Inspection

======================================================================

REQUIRED TOOLS

• Fish Tape

• Cable Pulling Equipment

• Punch Down Tool

• Cable Certification Tester

• Label Printer

• Cable Stripper

• Tone Generator

======================================================================

SAFETY & PPE REQUIREMENTS

Required PPE

□ Safety Glasses

□ Gloves

□ Dust Mask

Safety Requirements

• Avoid overloading cable bundles.

• Protect cable from abrasion.

• Restore all fire-rated penetrations.

• Maintain separation from electrical systems.

======================================================================

QUALITY CONTROL

Verify:

□ Four home runs installed

□ No splices

□ Proper bend radius

□ Proper bundle support

□ Service loops installed

□ Four cables certified

□ Labels installed

□ Photo documentation complete

======================================================================

INSPECTION & ACCEPTANCE CRITERIA

PASS when:

□ Four cables pass certification

□ Labels match documentation

□ Service loops verified

□ Photos uploaded

FAIL when:

□ Failed certification

□ Missing cable

□ Cable damage

□ Missing labels

□ Missing documentation

======================================================================

TESTING & DOCUMENTATION

Required Documentation

□ Cable Certification Report

□ Cable Identification Schedule

□ Patch Panel Port Assignment

□ Device Location Assignment

□ As-Built Documentation Updated

□ QR Code Applied (Future Standard)

======================================================================

LIFECYCLE MANAGEMENT

Expected Service Life

25+ Years

--------------------------------------------------

Preventive Maintenance

None Required

--------------------------------------------------

Replacement Criteria

Replace damaged or failed cable.

Entire home run replacement only.

--------------------------------------------------

Field Repairability

No field splicing permitted.

======================================================================

TRAINING REQUIREMENTS

Minimum Technician Level

Level-2 Technician

--------------------------------------------------

Required Certifications

Structured Cabling Certification

--------------------------------------------------

Required Hands-On Demonstration

Yes

--------------------------------------------------

Field Sign-Off Required

Yes

--------------------------------------------------

Estimated Training Time

4 Hours

--------------------------------------------------

Related Training Modules

Advanced Cable Routing

Bundle Management

Cable Certification

Structured Wiring

--------------------------------------------------

Competency Test Required

YES

======================================================================

ROOM COMPATIBILITY

ROOM-001 Great Room

ROOM-004 Home Office

ROOM-005 Media Room

ROOM-007 Bonus Room

ROOM-009 Kitchen

ROOM-020 Game Room

ROOM-023 Casita

ROOM-024 Outdoor Kitchen

ROOM-025 Home Bar

Future High-Density Data Locations

======================================================================

UPGRADE COMPATIBILITY

Compatible With:

• ASM-204 Six Cat6

• ASM-205 Fiber Backbone

• ASM-207 Wireless Access Point

• ASM-601 Structured Wiring Panel

• ASM-602 Equipment Rack

• ASM-606 Network Switch

======================================================================

INSTALLATION RULES

1.

All four cables shall be dedicated home runs.

--------------------------------------------------

2.

No splices shall be permitted.

--------------------------------------------------

3.

All four cables shall be individually certified.

--------------------------------------------------

4.

Labels shall be installed at both ends of every cable.

--------------------------------------------------

5.

Cable certification documentation shall be retained

with the project file.

--------------------------------------------------

6.

Every completed assembly shall include QC photos and

test reports.

======================================================================

COMMON ERRORS TO AVOID

• Missing cable

• Mixed routing paths

• Over-compressed cable bundle

• Improper bend radius

• Missing certification

• Missing labels

• Missing documentation

• Missing service loops

======================================================================

REFERENCED LIBRARIES

DD-058 Assembly Standards Library

PROD Library

MAT Library

LAB Library

ROOM Library

QC Library

ANSI/TIA-568 Standards

Installation Standards

======================================================================

REVISION APPROVAL

Engineering Approval

________________________

Operations Approval

________________________

Effective Date

________________________

Supersedes Version

N/A

Change Summary

Initial Release

======================================================================

END OF ASSEMBLY

ASM-203

======================================================================