======================================================================

DIGITALLY DEFINED

ASSEMBLY STANDARDS LIBRARY

ASSEMBLY ID:

ASM-202

ASSEMBLY NAME:

Dual Cat6 Home Run Assembly

VERSION:

1.0

STATUS:

FROZEN

======================================================================

ASSEMBLY METADATA

Assembly Category

Data Infrastructure

--------------------------------------------------

Assembly Type

Structured Cabling

--------------------------------------------------

Difficulty Level

2 of 5

--------------------------------------------------

Required Crew

1 Low-Voltage Technician

--------------------------------------------------

Estimated Labor

Automatically Generated

Referenced from LAB Library

--------------------------------------------------

Required Skill Level

Level-1 Technician

--------------------------------------------------

Dependencies

PROD Library

MAT Library

LAB Library

ROOM Library

QC Library

ANSI/TIA Structured Cabling Standards

======================================================================

PURPOSE

The Dual Cat6 Home Run Assembly establishes the standard

installation method for two dedicated Category 6 home run cables

installed from a device location to the Structured Wiring Closet.

This assembly provides redundant connectivity, supports multiple

networked devices, and ensures long-term flexibility for future

technology upgrades without requiring additional cable installation.

======================================================================

STANDARD APPLICATIONS

Approved For

• Premium Television Locations

• Home Offices

• Great Rooms

• Wireless Access Points

• Smart Home Controllers

• Security Panels

• Media Cabinets

• Outdoor Television Locations

• Future Expansion Locations

======================================================================

STANDARD SCOPE

This assembly includes:

• Two Cat6 home runs

• One low-voltage bracket

• Device-end service loops

• Panel-end service loops

• Permanent cable identification

• Cable certification

• Photo documentation

======================================================================

STANDARD INSTALLATION

Install two continuous Cat6 cables from the device location to the

Structured Wiring Closet.

Both cables shall follow the same routing pathway whenever practical.

No splices shall be permitted.

Support cables using approved fastening methods that do not deform

the cable jacket.

Maintain proper separation from electrical wiring and other sources

of electromagnetic interference.

======================================================================

CABLE REQUIREMENTS

Cable Type

Category 6

--------------------------------------------------

Topology

Dual Home Run

--------------------------------------------------

Maximum Length

90 Meters (295 Feet)

Per Cable

--------------------------------------------------

Termination

TIA-568B

Unless project documentation specifies otherwise.

======================================================================

INSTALLATION REQUIREMENTS

Maintain minimum bend radius:

4x Cable Diameter

--------------------------------------------------

Maintain cable spacing to prevent crushing.

--------------------------------------------------

Do not over-tighten cable supports.

--------------------------------------------------

Provide service loops:

Device End

12"

Panel End

36"

======================================================================

REQUIRED PRODUCTS

Automatically Generated

Referenced from:

PROD Library

======================================================================

BILL OF MATERIALS (BOM)

Referenced Automatically

PROD Library

MAT Library

LAB Library

Typical References

PROD-XXXX   Category 6 Cable

PROD-XXXX   Keystone Jack

PROD-XXXX   Faceplate

MAT-XXXX    Cable Label

MAT-XXXX    Velcro Strap

MAT-XXXX    Low-Voltage Bracket

LAB-XXXX    Pull Cat6

LAB-XXXX    Terminate Cat6

LAB-XXXX    Cable Certification

======================================================================

REQUIRED MATERIALS

Automatically Generated

Referenced from:

MAT Library

Typical materials include:

• Category 6 Cable

• Keystone Jacks

• Faceplate

• Cable Labels

• Velcro Straps

• Low-Voltage Bracket

======================================================================

REQUIRED LABOR

Automatically Generated

Referenced from:

LAB Library

Typical operations include:

• Layout

• Pull Dual Cat6

• Secure Cables

• Install Bracket

• Terminate Both Cables

• Label Cables

• Certification Testing

• Photograph Installation

• QC Inspection

======================================================================

REQUIRED TOOLS

• Fish Tape

• Cable Pulling Equipment

• Punch Down Tool

• Cable Certification Tester

• Label Printer

• Cable Stripper

• Tone Generator

======================================================================

SAFETY & PPE REQUIREMENTS

Required PPE

□ Safety Glasses

□ Gloves

□ Dust Mask

Safety Requirements

• Protect cable from physical damage.

• Restore all fire-rated penetrations.

• Maintain separation from electrical systems.

• Follow ladder safety requirements.

======================================================================

QUALITY CONTROL

Verify:

□ Two continuous home runs installed

□ No splices

□ Proper bend radius maintained

□ Service loops installed

□ Both cables certified

□ Labels installed

□ Cable routing protected

□ Photo documentation complete

======================================================================

INSPECTION & ACCEPTANCE CRITERIA

PASS when:

□ Both cables pass certification

□ Labels match project documentation

□ Proper service loops provided

□ Photos uploaded

FAIL when:

□ Failed certification

□ Missing cable

□ Cable splice found

□ Missing labels

□ Incomplete documentation

======================================================================

LIFECYCLE MANAGEMENT

Expected Service Life

25+ Years

--------------------------------------------------

Preventive Maintenance

None Required

--------------------------------------------------

Replacement Criteria

Replace damaged or failed cable.

Replace entire home run.

--------------------------------------------------

Field Repairability

Entire cable replacement only.

No splicing permitted.

--------------------------------------------------

Warranty Classification

Permanent Infrastructure

======================================================================

TRAINING REQUIREMENTS

Minimum Technician Level

Level-1 Technician

--------------------------------------------------

Required Certifications

Structured Cabling Certification

--------------------------------------------------

Required Hands-On Demonstration

Yes

--------------------------------------------------

Field Sign-Off Required

Yes

--------------------------------------------------

Estimated Training Time

3 Hours

--------------------------------------------------

Related Training Modules

Cable Pulling

Termination

Cable Certification

Structured Wiring

--------------------------------------------------

Competency Test Required

YES

======================================================================

ROOM COMPATIBILITY

ROOM-001 Great Room

ROOM-004 Home Office

ROOM-005 Media Room

ROOM-006 Outdoor Living

ROOM-009 Kitchen

ROOM-020 Game Room

ROOM-023 Casita

ROOM-024 Outdoor Kitchen

ROOM-025 Home Bar

ROOM-026 Library

All future rooms requiring dual network connections.

======================================================================

UPGRADE COMPATIBILITY

Compatible With:

• ASM-203 Quad Cat6

• ASM-204 Six Cat6

• ASM-205 Fiber Backbone

• ASM-207 Wireless Access Point

• ASM-601 Structured Wiring Panel

• ASM-606 Network Switch

======================================================================

INSTALLATION RULES

1.

Every cable shall be a dedicated home run.

--------------------------------------------------

2.

No splices shall be permitted.

--------------------------------------------------

3.

Every cable shall be independently certified.

--------------------------------------------------

4.

Permanent labels shall be installed at both ends of

each cable.

--------------------------------------------------

5.

Only approved Category 6 cable shall be installed.

--------------------------------------------------

6.

Every completed assembly shall include QC photos and

test results.

======================================================================

COMMON ERRORS TO AVOID

• Missing second cable

• Mixed cable routing

• Improper bend radius

• Crushed cable

• Missing certification

• Missing labels

• Over-tightened cable supports

• Missing service loops

• Missing QC photographs

======================================================================

REFERENCED LIBRARIES

DD-058 Assembly Standards Library

PROD Library

MAT Library

LAB Library

ROOM Library

QC Library

ANSI/TIA-568 Standards

Installation Standards

======================================================================

REVISION APPROVAL

Engineering Approval

________________________

Operations Approval

________________________

Effective Date

________________________

Supersedes Version

N/A

Change Summary

Initial Release

======================================================================

END OF ASSEMBLY

ASM-202

======================================================================